## Electrical WorkPlan
Hajj Ali EXPANSION Emergency Site
ELECTRICAL WORKS
IMPLEMENTATION WORKPLAN - 5,300 Family Plots
DURATION : 75 DAYS ( CALENDER DAYS )
NO | ACTIVITIES | PLANNED START | PLANNED FINISH | % COMPLETE | February 2017 | March 2017 | April 2017
1 | DEMARCATION
2 | INSTALLATION OF POLES
3 | INSTALL LIGHT FITTING
4 | INSTALL ELECTICAL CABLE
5 | INSTALL TENSION CABLE
6 | INSTALL CASING BOARDS
7 | INSTALL GENERATOR
8 | INSTALL FUEL TANK
9 | OPERATION &MAINTENANCE& TESTING
10 | FUEL SUPPLY

## Blank
BILL OF QUANTITY
Technical Specification Note that all drawings must be presented to IOM Engineers for approval before works begin. Note that all samples must be approved by IOM Engineers prior to installation Site Visit is mandatory and all prices introduced are assumed to be informed.
Project Name: Street Lighting with 250 KVA Generator
Location: IOM Hajj Ali Emergency - EXPANSION SITE 5,480 Plots
Populaton : 5,480 Families Camp population
No. | Description | Unit | Quantity | Unit Price (IQD) | Total (IQD)
1 | Demarcation electrical line on the natural ground. Installing an indications for round steel pole, another for lattice & other for H- pole. Checking the space and alignement etc. | units | 400 |  |  | Setting out and demarcation for generator pad, fuel tank shall comly with Perkin technical data sheet specifications
2 | Supply & install steel round pole or( galvenized ) according to local / iraqi electrical diroctirate specifications including; (i) excavating 40cm*40cm *180cm depth for all types of soil. (ii) installing the pole in striaght line casting Class 25 concrete 1:2:4 concrete mix . casting neck of 25cm hieght at least. (iii) supply & fix steel U- channel 4" 1ml thicknes 6mm at 50cm less than the top of pole with fixing 3- isolaters 11kv spindle type . (iv) leveling the ground around the pole with simple compaction | pcs | 360 |  |  | Comply with local Iraqi electrical code . Pole type 11m - 25cm diameter , 9m- 25cm diameter and , 11m- 40cm diameter
3 | Supply & install steel lattice pole or( galvenized one) according to local electrical diroctirate specifications including; (i) excavating 80*80180cm for all types of soil . (ii) installing the pole linearly then casting 1:2:4 conceret with casting a neck of 25cm (iii) supply & fix a steel U- channel 140cm 6mm thickness with supplying & fixing disk isolators from both sides & spindle one at the top (iv) leveling the ground around with simple compacting | pcs | 40 |  |  | comply to local Iraqi electrical code . Pole type 11 meter - 40 cm diameter (carry tension cable)
4 | Supply & install street lighting fitting with arm not less than 1m length turkish type , water proof including sodium bulb 150w with chock good ceiling , clear opal glass, with all accessories( wiring , connecting, testing , fixing well,-----etc). According IOM supervisor advice, including all necessary ring circuit wiring with standard wires from main cable at lattice polesthat shall be operated independently with approved quality switch, necessary connection, commissioning and testing with approval of IOM engineer | pcs | 400 |  |  | comply to local Iraqi electrical code
5 | Supply & install hanging twist cables 3*120+50mm aluminum with tetion wire good quality, including hanging & tension acc., max. slag not exceed 30cm. | LM | 14000 |  |  | comply to local Iraqi electrical code
2
6 | Supply & install tension assemble( stay wire), including casting to a depth of 180cm,with adjustable tention screw. | Assembly ( nos) | 50 |  |  | comply to local Iraqi electrical code
2
7 | Supply & install L.V. water proof casing board with 2 circuits. Contactors BBC of 250A & suitable bass bar & 2photo cells 10A of good quality | lumpsum | 1 |  |  | comply to local Iraqi electrical code
8 | Supply & install 250KVA generator . Perkins Type USA original , cilent type manuel starting. Full protection control. Water cooled included l.V. breaker of 400-630A. Class 25 concrete base ( 1:2:4 ). Use twisted reinforment rebar 12 " diameter into 4m x 2.5m x 20cm concrete pad mounteed on vibration pad top of concrete base. Install BRC fencing around with metal door for operation and maintenence , shed constructed with roof for protection against rain. include O&M training to camp management officer. | lumpsum | 1 |  |  | 1) Generator should come with jacket cover and silencer installed 2) ensure fuel tank installed above ground with gravity flow.Safety operation measures in place 3) Shed construction , follow site engineer instruction 4) Good Grounding must be done using 3 Copper rods 1.5m length and diameter 5/8", with connecting by copper conductor 70mm, salt & coal are included with the work to obtain less than 3d Ohms resistance.
9 | Supply / deliver diesel fuel for 20 liters per hour , 18 hours operation per day for one 5000 liters fuel tank capacity | lumpsum | 1 |  |  | 6 months fuel supply 1) Maintenance should include replacement of parts and services 2) Keep fuel supply tank is safe storage 3) Fuel supplies coordinate with camp management
10 | Supply / install 2 nos Fuel tank capacity each 5000 liters raised above the Genset fuel tank for gravity flow with metal stand and reinforced concrete pad foundation. Install a fuel filter in the fuel tank | nos | 1
TOTAL