## Electrical WorkPlan
Qayyarah Emergency Site
ELECTRICAL WORKS
IMPLEMENTATION WORKPLAN - 5,000 Family Plots
DURATION : 30 DAYS ( CALENDER DAYS )
NO | ACTIVITIES | PLANNED START | PLANNED FINISH | % COMPLETE | March 2017 | April 2017
1 | DEMARCATION
2 | INSTALLATION OF POLES
3 | INSTALL LIGHT FITTING
4 | INSTALL ELECTICAL CABLE
5 | INSTALL TENSION CABLE
6 | INSTALL CASING BOARDS
7 | INSTALL GENERATOR
8 | INSTALL FUEL TANK
9 | OPERATION &MAINTENANCE& TESTING
10 | FUEL SUPPLY

## Blank
BILL OF QUANTITY
Project Name: Street Lighting with 250 KVA Generator
Location: Qayarah Emergency Site -Phase 2 - 5000 Family Plots
No. | Description | Unit | Quantity | Unit Price (IQD) | Total (IQD) | Technical Specification
1 | Demarcation electrical line on the natural ground. Installing an indications for round steel pole, another for lattice & other for H- pole. Checking the space and alignement etc. | units | 375 |  |  | Setting out and demarcation for generator pad, fuel tank shall comly with Perkin technical data sheet specifications (ii) Include main access road to sector A and Sector H. Refer drawing
2 | Supply & install steel round pole or( galvenized ) according to local / iraqi electrical diroctirate specifications including; (i) excavating 40cm*40cm *180cm depth for all types of soil. (ii) installing the pole in striaght line casting Class 25 concrete 1:2:4 concrete mix . casting neck of 25cm hieght at least. (iii) supply & fix steel U- channel 4" 1ml thicknes 6mm at 50cm less than the top of pole with fixing 3- isolaters 11kv spindle type . (iv) leveling the ground around the pole with simple compaction | pcs | 265 |  |  | Comply with local Iraqi electrical code . Pole type 11m - 25cm diameter , 9m- 25cm diameter and , 11m- 40cm diameter (ii) Include main access road to sector A and Sector H. Refer drawing
3 | Supply & install steel lattice pole or( galvenized one) according to local electrical diroctirate specifications including; (i) excavating 80*80180cm for all types of soil . (ii) installing the pole linearly then casting 1:2:4 conceret with casting a neck of 25cm (iii) supply & fix a steel U- channel 140cm 6mm thickness with supplying & fixing disk isolators from both sides & spindle one at the top (iv) leveling the ground around with simple compacting | pcs | 110 |  |  | comply to local Iraqi electrical code . Pole type 11 meter - 40 cm diameter (carry tension cable) (ii) Include main access road to sector A and Sector H. Refer drawing
4 | Supply & install street lighting fitting with arm not less than 1m length turkish type IP 65 rated , water proof including sodium bulb 250w with chock good ceiling , clear opal glass, with all accessories( wiring , connecting, testing , fixing well,-----etc). According IOM supervisor advice | pcs | 375 |  |  | comply to local Iraqi electrical code
5 | Supply & install hanging twist cables 3*120+50mm aluminum with tetion wire good quality, including hanging & tention acc., max. slag not exceed 30cm. | LM | 16500 |  |  | comply to local Iraqi electrical code
2
6 | Supply & install tension assemble( stay wire), including casting to a depth of 180cm,with adjustable tention screw. | Assembly ( nos) | 50 |  |  | comply to local Iraqi electrical code
2
7 | Supply & install L.V. water proof casing board with 2 circuits. Contactors BBC of 250A & suitable bass bar & 2photo cells 10A of good quality | lumpsum | 1 |  |  | comply to local Iraqi electrical code
8 | Supply & install 250KVA generator . Perkins Type USA original , cilent type manuel starting. Full protection control. Water cooled included l.V. breaker of 400-630A. Class 25 concrete base ( 1:2:4 ). Use twisted reinforment rebar 12 " diameter into 4m x 2.5m x 20cm concrete pad mounteed on vibration pad top of concrete base. Install BRC fencing around with metal door for operation and maintenence , shed constructed with roof for protection against rain. include O&M training to camp management officer. | lumpsum | 1 |  |  | 1) Generator should come with jacket cover and silencer installed 2) ensure fuel tank installed above ground with gravity flow.Safety operation measures in place 3) Shed construction , follow site engineer instruction 4) Good Grounding must be done using 3 Copper rods 1.5m length and diameter 5/8", with connecting by copper conductor 70mm, salt & coal are included with the work to obtain less than 3d Ohms resistance.
9 | Supply / deliver diesel fuel for 20 liters per hour , 18 hours operation per day for one 5000 liters fuel tank capacity | lumpsum | 1 |  |  | 6 months fuel supply 1) Maintenance should include replacement of parts and services 2) Keep fuel supply tank is safe storage 3) Fuel supplies coordinate with camp management
10 | Supply / install 2 nos Fuel tank capacity each 5000 liters raised above the Genset fuel tank for gravity flow with metal stand and reinforced concrete pad foundation. Install a fuel filter in the fuel tank | nos | 1
TOTAL